## Introduction
BANZ Technical Guide 14
Lifecycle analysis of heat plants
Introduction to financial model
This financial model provides the methodology and tools for calculating the LCOE (levelised cost of energy) from a range of fuel and technology options
It is a companion to the BANZ Technical Guide 14: Best practice guideline for life cycle analysis of heat plant projects
A description of the model is in Section 6 of the Guide, and
Instructions for use are detailed in Section 7 of the Guide
The Guide and this model can be downloaded from: | https://www.bioenergy.org.nz/resource/tg14-Life-cycle-analysis-heat-plant
Note: this financial model has some cells hidden and others, not required for data input, are locked

## Capital
BANZ Technical Guide 14
Lifecycle analysis of heat plants | Option | 1 | 2 | 3 | 4 | 5 | 6 | 7
Sheet 1: Capital costs
|  | Wood chip (dry) | Wood chip (wet) | Diesel, LFO | LPG | Electricity (direct use) | Electricity (heat pump) | Coal
Boiler including fuel handling, de-ashing,emission control equipment and ancillary systems, or alternative heat plant
Per quotation |  | 5000000 | 5000000 | 900000 | 750000 | 500000 | 400000 | 4500000
Required to cover exclusions
Installation and commissioning
Spares, tools and stores
Heat distribution system cost
Sub total |  | 5000000 | 5000000 | 900000 | 750000 | 500000 | 400000 | 4500000
Ancillary and site works
Siteworks, civil costs, piling and foundations,
Fuel storage and processing: storage bin, reclaim system, drying, loaders, conveyors
Buildings: boiler house, control room, maintenance workshop, ablutions, lunchroom
Roading, paving, stormwater & landscaping
Water supply and treatment, effluent/sanitory disposal
Ash disposal systems, bins, handling equipment
Electrical supply interconnection
Security fencing, fire protection and alarm systems
Lighting, including security lighting
Remote control and monitoring systems
Integration of controls with existing plant
Sub total |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Consultants and services
Engineering and design
Geotech investigations and civil design
Mechanical, process and electrical
Environmental
Project management
Project insurance
Legal, building consents and other fees
Staff recruitment and training
Standard procedures, manuals & documents
Sub total |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total, ex-contingencies |  | 5000000 | 5000000 | 900000 | 750000 | 500000 | 400000 | 4500000
Contingencies @ | 20% | 1000000 | 1000000 | 180000 | 150000 | 100000 | 80000 | 900000
Total including contingencies |  | 6000000 | 6000000 | 1080000 | 900000 | 600000 | 480000 | 5400000

## O&M
BANZ Technical Guide 14
Lifecycle analysis of heat plants
Sheet 2: Operating and maintenance costs
|  | Wood chip (dry) | Wood chip (wet) | Diesel, LFO | LPG | Electricity (direct use) | Electricity (heat pump) | Coal
| Operations and maintenance staff | 40000 | 40000 | 40000 | 25000 | 14000 | 10000 | 30000
Parasitic electricity consumption
Other consumables
| Maintenance contract | 40000 | 50000 |  |  |  |  | 40000
Annual plant shut/overhall
Callouts and breakages
Insurance
Ash disposal:
Cost of disposal (i.e. to landfill)
Service contractor costs
| Total annual cost | 80000 | 90000 | 40000 | 25000 | 14000 | 10000 | 70000

## Fuel
BANZ Technical Guide 14 |  |  |  |  | Do we need to inflate
Lifecycle analysis of heat plants
Sheet 3: Fuel costs
[5 empty] | Wood chip (dry) | Wood chip (wet) | Diesel, LFO | LPG | Electricity (direct use) | Electricity (heat pump) | Coal
| Heat required (GJ) | 300000 |  |  | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000
|  | Heat production efficiency (gross) |  | % | 73% | 62% | 80% | 90% | 98% | 4 | 75% | COP in case of heat pumps
|  | Fuel requirement (calculated) |  | GJ | 410958.9041 | 483870.9677 | 375000 | 333333.3333 | 306122.449 | 75000 | 400000
|  | Fuel cost per GJ |  | $ | 11.11 | 7.4 | 30.26 | 25 | 20 | 20 | 8
|  | Ann. cost of fuel (ex carbon cost) |  | $ | 4565753.4247 | 3580645.1613 | 11347500 | 8333333.3333 | 6122448.9796 | 1500000 | 3200000
|  | Emission factor (KT CO2/PJ) |  |  | 0 | 0 | 80 | 60 | 0 | 0 | 90
|  | Annual tonnes of CO2 |  |  | 0 | 0 | 24000 | 18000 | 0 | 0 | 27000
|  |  | From | Rate/
|  |  | year | tonne
|  | Annual emmission cost from year: | 1 | 25 | 0 | 0 | 600000 | 450000 | 0 | 0 | 675000
|  | Annual emmission cost from year: | 6 | 60 | 0 | 0 | 1440000 | 1080000 | 0 | 0 | 1620000
|  | Annual emmission cost from year: | 12 | 120 | 0 | 0 | 2880000 | 2160000 | 0 | 0 | 3240000
From year
|  | Annual cost of fuel (incl carbon cost) | 1 |  | 4565753.4247 | 3580645.1613 | 11947500 | 8783333.3333 | 6122448.9796 | 1500000 | 3875000
|  | Annual cost of fuel (incl carbon cost) | 6 |  | 4565753.4247 | 3580645.1613 | 12787500 | 9413333.3333 | 6122448.9796 | 1500000 | 4820000
|  | Annual cost of fuel (incl carbon cost) | 12 |  | 4565753.4247 | 3580645.1613 | 14227500 | 10493333.3333 | 6122448.9796 | 1500000 | 6440000
[5 empty] | Wood chip | Wood pellets | Diesel, fuel oil | Natural gas or LPG | Electricity (direct use) | Electricity (heat pump) | Coal
Notes: |  | Typical fuel conversion efficiency, by fuel (gross) |  |  | In range 62 to 73%, dep. on moisture | 73% | 80-85% | 85% | Nominally 100% | COP say 3.5, up to 5 for commercial scale facilities | Up to 80%, depending on moisture content
Indicative wood fuel calorific value (gross)
|  | Pinus radiata |  |  | Seasoned chip: 30% moisture content, 13.5GJ/tonne
Partially seasoned chip: 40% mosture content, 11.5 GJ/tonne
Green wood chip: circa 50% mositure content, 8GJ/tonne
|  | Other fuels |  |  | Diesel, fuel oil: 42 GJ/tonne
Natural gas, LPG: 54 GJ/tonne
Coal: from 15 GJ/tonne (lignite) to 22 GJ/tonne (sub-bituminous)

## Inputs
BANZ Technical Guide 14
Lifecycle analysis of heat plants
Sheet 4: Modelling inputs
HEAT REQUIRED GJ | 300000 | Wood chip (dry) | Wood chip (wet) | Diesel, LFO | LPG | Electricity (direct use) | Electricity (heat pump) | Coal
INPUT FOR EACH FUEL SCENARIO
Total capital including contingencies |  | 6000000 | 6000000 | 1080000 | 900000 | 600000 | 480000 | 5400000
Total annual cost (O&M) |  | 80000 | 90000 | 40000 | 25000 | 14000 | 10000 | 70000
Annual fuel cost year 1 |  | 4565753.4247 | 3580645.1613 | 11347500 | 8333333.3333 | 6122448.9796 | 1500000 | 3200000
Annual emmission cost from Year | 1 | 0 | 0 | 600000 | 450000 | 0 | 0 | 675000
Annual emmission cost from Year | 6 | 0 | 0 | 1440000 | 1080000 | 0 | 0 | 1620000
Annual emmission cost from Year | 12 | 0 | 0 | 2880000 | 2160000 | 0 | 0 | 3240000
Fuel inflation rate (above normal inflation) |  | 2% | 2% | 2% | 2% | 5% | 5% | 10%
Residual value (% of original cost) |  | 25% | 25% | 0% | 35% | 35% | 25% | 25%
Additional benefits/costs (NEGATIVE IF A COST) | (Per annum)
Additional benefit/cost (NEGATIVE IF A COST) | (Year 1)
Financial information (common)
WACC (real) | 6.8%
Project life (years) for modelling | 20

## Outputs
BANZ Technical Guide 14
Lifecycle analysis of heat plants
| Sheet 5: Modelling outputs |  | For heat requirement of |  | 300000 | GJ
| Scenario | Annual heat cost Year 1 | NPV (pre-tax) | Levelised heat cost per GJ | Levelised heat cost per kWh
| Wood chip (dry) | 4645753.4247 | -63659947.6007 | 19.7199 | 0.070992
| Wood chip (wet) | 3670645.1613 | -51425743.0438 | 15.9301 | 0.057348
| Diesel, LFO | 11987500 | -160225467.6576 | 49.6329 | 0.17868
| LPG | 8808333.3333 | -117953939.0748 | 36.5385 | 0.13154
| Electricity (direct use) | 6136448.9796 | -98719882.6009 | 30.5804 | 0.11009
| Electricity (heat pump) | 1510000 | -24762771.5955 | 7.6707 | 0.027615
| Coal | 3945000 | -104970280.7407 | 32.5165 | 0.11706
Excluding
capital recovery
| Sensitivities | Levelised heat cost per GJ for heat requirement of |  |  |  |  | 300000 | GJ
|  | Capital cost |  | Fuel cost |  | O&M |  | Heat load
|  | Plus 20% | Minus 10% | Plus 20% | Minus 10% | Plus 20% | Minus 10% | Plus 20% | Minus 20%
| Wood chip | 20.0916 | 19.534 | 21.1374 | 17.9479 | 19.7412 | 19.6932 | 19.3864 | 20.22
| Wood pellets | 19.1161 | 14.3371 | 17.0418 | 14.5405 | 15.9901 | 15.9001 | 15.5911 | 16.4386
| Diesel, fuel oil | 49.6596 | 49.5994 | 58.465 | 47.3247 | 49.8595 | 36.5301 | 49.5586 | 49.7442
| Natural gas or LPG | 36.5608 | 36.5106 | 43.1075 | 34.8761 | 36.5451 | 36.5301 | 36.4825 | 36.6225
| Electricity (direct use) | 30.5952 | 30.5618 | 33.0096 | 27.5438 | 30.5841 | 30.5757 | 30.5445 | 30.6341
| Electricity (Heat pump) | 7.6826 | 7.6559 | 6.9268 | 7.6707 | 7.6674 | 7.6707 | 7.6322 | 7.7285
| Coal | 32.6414 | 32.3605 | 46.5008 | 34.7563 | 32.5352 | 32.4932 | 32.2175 | 32.965

## Option 1
BANZ Technical Guide 14
Lifecycle analysis of heat plants
Sheet 6, DCF model: | Wood chip (dry)
|  |  | Costs NPV |  | -63659947.6007
|  |  | Energy NPV |  | 3228212.8571
|  |  | Levelised cost per GJ |  | 19.7199
Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Trigger Cell |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
Costs
Capital Cost of Plant | 6000000
Residual value |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1500000 | 0 | 0 | 0 | 0 | 0
Fuel cost |  | 4565753.4247 | 4657068.4932 | 4750209.863 | 4845214.0603 | 4942118.3415 | 5040960.7083 | 5141779.9225 | 5244615.5209 | 5349507.8313 | 5456497.988 | 5565627.9477 | 5676940.5067 | 5790479.3168 | 5906288.9032 | 6024414.6812 | 6144902.9748 | 6267801.0343 | 6393157.055 | 6521020.1961 | 6651440.6 | 0 | 0 | 0 | 0 | 0
Carbon cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
O&M |  | 80000 | 80000 | 80000 | 80000 | 80000 | 80000 | 80000 | 80000 | 80000 | 80000 | 80000 | 80000 | 80000 | 80000 | 80000 | 80000 | 80000 | 80000 | 80000 | 80000 | 0 | 0 | 0 | 0 | 0
Additional benefits/costs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total annual costs | 6000000 | 4645753.4247 | 4737068.4932 | 4830209.863 | 4925214.0603 | 5022118.3415 | 5120960.7083 | 5221779.9225 | 5324615.5209 | 5429507.8313 | 5536497.988 | 5645627.9477 | 5756940.5067 | 5870479.3168 | 5986288.9032 | 6104414.6812 | 6224902.9748 | 6347801.0343 | 6473157.055 | 6601020.1961 | 5231440.6 | 0 | 0 | 0 | 0 | 0
Energy output (GJ) |  | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 0 | 0 | 0 | 0 | 0
Fuel plus Carbon costs | 0 | 4565753.4247 | 4657068.4932 | 4750209.863 | 4845214.0603 | 4942118.3415 | 5040960.7083 | 5141779.9225 | 5244615.5209 | 5349507.8313 | 5456497.988 | 5565627.9477 | 5676940.5067 | 5790479.3168 | 5906288.9032 | 6024414.6812 | 6144902.9748 | 6267801.0343 | 6393157.055 | 6521020.1961 | 6651440.6 | 0 | 0 | 0 | 0 | 0
SENSITIVITIES
| Capital |  |  | 19.7199 |  | 20% | Load plus 20% | Load -20%
|  | minus 10% | 5400000
|  | plus 20% | 7200000 |  |  | -11440299.6935 | -75100247.2942 | -52219647.9072
[6 empty] | 645642.5714 | 3873855.4285 | 2582570.2857
[7 empty] | 19.3864 | 20.22
| Fuel |  |  | 19.7199
|  | minus 10% | 4109178.0822
|  | plus 20% | 5478904.1096
| O&M |  |  | 19.7199
|  | minus 10% | 72000
|  | plus 20% | 96000

## Option 2
DCF (Discounted Cash Flow) Analysis
Lifecycle analysis of heat plants
Sheet 7, DCF model: | Wood chip (wet)
|  |  | Costs NPV |  | -51425743.0438
|  |  | Energy NPV |  | 3228212.8571
|  |  | Levelised cost per GJ |  | 15.9301
Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Trigger Cell |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
Costs
Capital Cost of Plant | 6000000
Residual value |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1500000 | 0 | 0 | 0 | 0 | 0
Fuel cost |  | 3580645.1613 | 3652258.0645 | 3725303.2258 | 3799809.2903 | 3875805.4761 | 3953321.5857 | 4032388.0174 | 4113035.7777 | 4195296.4933 | 4279202.4231 | 4364786.4716 | 4452082.201 | 4541123.845 | 4631946.3219 | 4724585.2484 | 4819076.9534 | 4915458.4924 | 5013767.6623 | 5114043.0155 | 5216323.8758 | 0 | 0 | 0 | 0 | 0
Carbon cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
O&M |  | 90000 | 90000 | 90000 | 90000 | 90000 | 90000 | 90000 | 90000 | 90000 | 90000 | 90000 | 90000 | 90000 | 90000 | 90000 | 90000 | 90000 | 90000 | 90000 | 90000 | 0 | 0 | 0 | 0 | 0
Additional benefits/costs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total annual costs | 6000000 | 3670645.1613 | 3742258.0645 | 3815303.2258 | 3889809.2903 | 3965805.4761 | 4043321.5857 | 4122388.0174 | 4203035.7777 | 4285296.4933 | 4369202.4231 | 4454786.4716 | 4542082.201 | 4631123.845 | 4721946.3219 | 4814585.2484 | 4909076.9534 | 5005458.4924 | 5103767.6623 | 5204043.0155 | 3806323.8758 | 0 | 0 | 0 | 0 | 0
Energy output (GJ) |  | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 0 | 0 | 0 | 0 | 0
Fuel plus Carbon costs |  | 3580645.1613 | 3652258.0645 | 3725303.2258 | 3799809.2903 | 3875805.4761 | 3953321.5857 | 4032388.0174 | 4113035.7777 | 4195296.4933 | 4279202.4231 | 4364786.4716 | 4452082.201 | 4541123.845 | 4631946.3219 | 4724585.2484 | 4819076.9534 | 4915458.4924 | 5013767.6623 | 5114043.0155 | 5216323.8758 | 0 | 0 | 0 | 0 | 0
SENSITIVITIES
| Capital | 100% |  | 15.9301 |  | 20% | Load plus 20% | Load -20%
|  | minus 10% | 5400000
|  | plus 20% | 7200000 |  |  | -8971937.3631 | -60397680.4069 | -42453805.6808
[6 empty] | 645642.5714 | 3873855.4285 | 2582570.2857
[7 empty] | 15.5911 | 16.4386
| Fuel | 100% |  | 15.9301
|  | minus 10% | 3222580.6452
|  | plus 20% | 4296774.1935
| O&M | 100% |  | 15.9301
|  | minus 10% | 81000
|  | plus 20% | 108000

## Option 3
DCF (Discounted Cash Flow) Analysis
Lifecycle analysis of heat plants
Sheet 8, DCF model: | Diesel, LFO
|  |  | Costs NPV |  | -160225467.6576
|  |  | Energy NPV |  | 3228212.8571
49.6329
Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Trigger Cell |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
Costs
Capital Cost of Plant | 1080000
Residual value |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -270000 | 0 | 0 | 0 | 0 | 0
Fuel cost |  | 11347500 | 11574450 | 11805939 | 12042057.78 | 12282898.9356 | 12528556.9143 | 12779128.0526 | 13034710.6137 | 13295404.8259 | 13561312.9224 | 13832539.1809 | 14109189.9645 | 14391373.7638 | 14679201.2391 | 14972785.2639 | 15272240.9691 | 15577685.7885 | 15889239.5043 | 16207024.2944 | 16531164.7803 | 0 | 0 | 0 | 0 | 0
Carbon cost |  | 600000 | 600000 | 600000 | 600000 | 600000 | 1440000 | 1440000 | 1440000 | 1440000 | 1440000 | 1440000 | 2880000 | 2880000 | 2880000 | 2880000 | 2880000 | 2880000 | 2880000 | 2880000 | 2880000 | 0 | 0 | 0 | 0 | 0
O&M |  | 40000 | 40000 | 40000 | 40000 | 40000 | 40000 | 40000 | 40000 | 40000 | 40000 | 40000 | 40000 | 40000 | 40000 | 40000 | 40000 | 40000 | 40000 | 40000 | 40000 | 0 | 0 | 0 | 0 | 0
Additional benefits/costs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total annual costs | 1080000 | 11987500 | 12214450 | 12445939 | 12682057.78 | 12922898.9356 | 14008556.9143 | 14259128.0526 | 14514710.6137 | 14775404.8259 | 15041312.9224 | 15312539.1809 | 17029189.9645 | 17311373.7638 | 17599201.2391 | 17892785.2639 | 18192240.9691 | 18497685.7885 | 18809239.5043 | 19127024.2944 | 19181164.7803 | 0 | 0 | 0 | 0 | 0
Energy output (GJ) |  | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 0 | 0 | 0 | 0 | 0
Fuel plus Carbon costs |  | 11947500 | 12174450 | 12405939 | 12642057.78 | 12882898.9356 | 13968556.9143 | 14219128.0526 | 14474710.6137 | 14735404.8259 | 15001312.9224 | 15272539.1809 | 16989189.9645 | 17271373.7638 | 17559201.2391 | 17852785.2639 | 18152240.9691 | 18457685.7885 | 18769239.5043 | 19087024.2944 | 19411164.7803 | 0 | 0 | 0 | 0 | 0
SENSITIVITIES
| Capital | 100% |  | 49.6329 |  | 20% | Load plus 20% | Load -20%
|  | minus 10% | 972000
|  | plus 20% | 1296000 |  |  | -31757494.53 | -191982962.1875 | -128467973.1276
[6 empty] | 645642.5714 | 3873855.4285 | 2582570.2857
[7 empty] | 49.5586 | 49.7442
| Fuel | 100% |  | 49.6329
|  | minus 10% | 10752750
|  | plus 20% | 14337000
| O&M | 100% |  | 49.6329
|  | minus 10% | 81000
|  | plus 20% | 108000

## Option 4
DCF (Discounted Cash Flow) Analysis
Lifecycle analysis of heat plants
Sheet 9, DCF model: | LPG
|  |  | Costs NPV |  | -117953939.0748
|  |  | Energy NPV |  | 3228212.8571
36.5385
Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Trigger Cell |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
Costs
Capital Cost of Plant | 900000
Residual value |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -315000 | 0 | 0 | 0 | 0 | 0
Fuel cost |  | 8333333.3333 | 8500000 | 8670000 | 8843400 | 9020268 | 9200673.36 | 9384686.8272 | 9572380.5637 | 9763828.175 | 9959104.7385 | 10158286.8333 | 10361452.57 | 10568681.6214 | 10780055.2538 | 10995656.3589 | 11215569.486 | 11439880.8758 | 11668678.4933 | 11902052.0631 | 12140093.1044 | 0 | 0 | 0 | 0 | 0
Carbon cost |  | 450000 | 450000 | 450000 | 450000 | 450000 | 1080000 | 1080000 | 1080000 | 1080000 | 1080000 | 1080000 | 2160000 | 2160000 | 2160000 | 2160000 | 2160000 | 2160000 | 2160000 | 2160000 | 2160000 | 0 | 0 | 0 | 0 | 0
O&M |  | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 0 | 0 | 0 | 0 | 0
Additional benefits/costs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total annual costs | 900000 | 8808333.3333 | 8975000 | 9145000 | 9318400 | 9495268 | 10305673.36 | 10489686.8272 | 10677380.5637 | 10868828.175 | 11064104.7385 | 11263286.8333 | 12546452.57 | 12753681.6214 | 12965055.2538 | 13180656.3589 | 13400569.486 | 13624880.8758 | 13853678.4933 | 14087052.0631 | 14010093.1044 | 0 | 0 | 0 | 0 | 0
Energy output (GJ) |  | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 0 | 0 | 0 | 0 | 0
Fuel plus Carbon costs |  | 8783333.3333 | 8950000 | 9120000 | 9293400 | 9470268 | 10280673.36 | 10464686.8272 | 10652380.5637 | 10843828.175 | 11039104.7385 | 11238286.8333 | 12521452.57 | 12728681.6214 | 12940055.2538 | 13155656.3589 | 13375569.486 | 13599880.8758 | 13828678.4933 | 14062052.0631 | 14300093.1044 | 0 | 0 | 0 | 0 | 0
SENSITIVITIES
| Capital | 100% |  | 36.5385 |  | 20% | Load plus 20% | Load -20%
|  | minus 10% | 810000
|  | plus 20% | 1080000 |  |  | -23373885.3878 | -141327824.4626 | -94580053.6871
[6 empty] | 645642.5714 | 3873855.4285 | 2582570.2857
[7 empty] | 36.4825 | 36.6225
| Fuel | 100% |  | 36.5385
|  | minus 10% | 7905000
|  | plus 20% | 10540000
| O&M | 100% |  | 36.5385
|  | minus 10% | 22500
|  | plus 20% | 30000

## Option 5
BANZ Technical Guide 14
Lifecycle analysis of heat plants
Sheet 10, DCF model: | Electricity (direct use)
|  |  | Costs NPV |  | -98719882.6009
|  |  | Energy NPV |  | 3228212.8571
|  |  | Levelised cost per GJ |  | 30.5804
Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Trigger Cell |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
Costs
Capital Cost of Plant | 600000
Residual value |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -210000 | 0 | 0 | 0 | 0 | 0
Fuel cost |  | 6122448.9796 | 6428571.4286 | 6750000 | 7087500 | 7441875 | 7813968.75 | 8204667.1875 | 8614900.5469 | 9045645.5742 | 9497927.8529 | 9972824.2456 | 10471465.4579 | 10995038.7307 | 11544790.6673 | 12122030.2006 | 12728131.7107 | 13364538.2962 | 14032765.211 | 14734403.4716 | 15471123.6452 | 0 | 0 | 0 | 0 | 0
Carbon cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
O&M |  | 14000 | 14000 | 14000 | 14000 | 14000 | 14000 | 14000 | 14000 | 14000 | 14000 | 14000 | 14000 | 14000 | 14000 | 14000 | 14000 | 14000 | 14000 | 14000 | 14000 | 0 | 0 | 0 | 0 | 0
Additional benefits/costs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total annual costs | 600000 | 6136448.9796 | 6442571.4286 | 6764000 | 7101500 | 7455875 | 7827968.75 | 8218667.1875 | 8628900.5469 | 9059645.5742 | 9511927.8529 | 9986824.2456 | 10485465.4579 | 11009038.7307 | 11558790.6673 | 12136030.2006 | 12742131.7107 | 13378538.2962 | 14046765.211 | 14748403.4716 | 15275123.6452 | 0 | 0 | 0 | 0 | 0
Energy output (GJ) |  | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 0 | 0 | 0 | 0 | 0
Fuel plus Carbon costs |  | 6122448.9796 | 6428571.4286 | 6750000 | 7087500 | 7441875 | 7813968.75 | 8204667.1875 | 8614900.5469 | 9045645.5742 | 9497927.8529 | 9972824.2456 | 10471465.4579 | 10995038.7307 | 11544790.6673 | 12122030.2006 | 12728131.7107 | 13364538.2962 | 14032765.211 | 14734403.4716 | 15471123.6452 | 0 | 0 | 0 | 0 | 0
SENSITIVITIES
| Capital | 100% |  | 30.5804 |  | 20% | Load plus 20% | Load -20%
|  | minus 10% | 540000
|  | plus 20% | 720000 |  |  | -19605113.9471 | -118324996.5481 | -79114768.6538
[6 empty] | 645642.5714 | 3873855.4285 | 2582570.2857
[7 empty] | 30.5445 | 30.6341
| Fuel | 100% |  | 30.5804
|  | minus 10% | 5510204.0816
|  | plus 20% | 7346938.7755
| O&M | 100% |  | 30.5804
|  | minus 10% | 12600
|  | plus 20% | 16800

## Option 6
BANZ Technical Guide 14
Lifecycle analysis of heat plants
Sheet 11, DCF model: | Electricity (heat pump)
|  |  | Costs NPV |  | -24762771.5955
Plant replacement (years) | 15 |  | Energy NPV |  | 3228212.8571
|  |  | Levelised cost per GJ |  | 7.6707
Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Trigger Cell |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
Costs
Capital Cost of Plant | 480000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 480000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Residual value |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -120000 | 0 | 0 | 0 | 0 | 0
Fuel cost |  | 1500000 | 1575000 | 1653750 | 1736437.5 | 1823259.375 | 1914422.3438 | 2010143.4609 | 2110650.634 | 2216183.1657 | 2326992.324 | 2443341.9402 | 2565509.0372 | 2693784.489 | 2828473.7135 | 2969897.3992 | 3118392.2691 | 3274311.8826 | 3438027.4767 | 3609928.8505 | 3790425.2931 | 0 | 0 | 0 | 0 | 0
Carbon cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
O&M |  | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 0 | 0 | 0 | 0 | 0
Additional benefits/costs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total annual costs | 480000 | 1510000 | 1585000 | 1663750 | 1746437.5 | 1833259.375 | 1924422.3438 | 2020143.4609 | 2120650.634 | 2226183.1657 | 2336992.324 | 2453341.9402 | 2575509.0372 | 2703784.489 | 3318473.7135 | 2979897.3992 | 3128392.2691 | 3284311.8826 | 3448027.4767 | 3619928.8505 | 3680425.2931 | 0 | 0 | 0 | 0 | 0
Energy output (GJ) |  | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 0 | 0 | 0 | 0 | 0
Fuel plus Carbon costs |  | 1500000 | 1575000 | 1653750 | 1736437.5 | 1823259.375 | 1914422.3438 | 2010143.4609 | 2110650.634 | 2216183.1657 | 2326992.324 | 2443341.9402 | 2565509.0372 | 2693784.489 | 2828473.7135 | 2969897.3992 | 3118392.2691 | 3274311.8826 | 3438027.4767 | 3609928.8505 | 3790425.2931 | 0 | 0 | 0 | 0 | 0
SENSITIVITIES
|  |  |  | Levelised cost per GJ |  | 20% | Load plus 20% | Load -20%
| Capital | 100% |  | 7.6707
|  | minus 10% | 432000 |  |  | -4803252.917 | -29566024.5125 | -19959518.6784
|  | plus 20% | 576000 |  |  | 645642.5714 | 3873855.4285 | 2582570.2857
[7 empty] | 7.6322 | 7.7285
| Fuel |  |  | Levelised cost per GJ
|  | 100% |  | 7.6707
|  | minus 10% | 1350000
|  | plus 20% | 1800000
O&M
|  | 100% |  | 7.6707
|  | minus 10% | 9000
|  | plus 20% | 12000

## Option 7
BANZ Technical Guide 14
Lifecycle analysis of heat plants
Sheet 12, DCF model: | Coal
O&M | 70000
|  |  | Costs NPV |  | -104970280.7407
Capital cost | 5400000 |  | Energy NPV |  | 3228212.8571
|  |  | Levelised cost per GJ |  | 32.5165
Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Trigger Cell |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
Costs
Capital Cost of Plant | 5400000
Residual value |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1350000 | 0 | 0 | 0 | 0 | 0
Fuel cost |  | 3200000 | 3520000 | 3872000 | 4259200 | 4685120 | 5153632 | 5668995.2 | 6235894.72 | 6859484.192 | 7545432.6112 | 8299975.8723 | 9129973.4596 | 10042970.8055 | 11047267.8861 | 12151994.6747 | 13367194.1421 | 14703913.5563 | 16174304.912 | 17791735.4032 | 19570908.9435 | 0 | 0 | 0 | 0 | 0
Carbon cost |  | 675000 | 675000 | 675000 | 675000 | 675000 | 1620000 | 1620000 | 1620000 | 1620000 | 1620000 | 1620000 | 3240000 | 3240000 | 3240000 | 3240000 | 3240000 | 3240000 | 3240000 | 3240000 | 3240000 | 0 | 0 | 0 | 0 | 0
O&M |  | 70000 | 70000 | 70000 | 70000 | 70000 | 70000 | 70000 | 70000 | 70000 | 70000 | 70000 | 70000 | 70000 | 70000 | 70000 | 70000 | 70000 | 70000 | 70000 | 70000 | 0 | 0 | 0 | 0 | 0
Additional benefits/costs |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total annual costs | 5400000 | 3945000 | 4265000 | 4617000 | 5004200 | 5430120 | 6843632 | 7358995.2 | 7925894.72 | 8549484.192 | 9235432.6112 | 9989975.8723 | 12439973.4596 | 13352970.8055 | 14357267.8861 | 15461994.6747 | 16677194.1421 | 18013913.5563 | 19484304.912 | 21101735.4032 | 21530908.9435 | 0 | 0 | 0 | 0 | 0
Energy output (GJ) |  | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 300000 | 0 | 0 | 0 | 0 | 0
Fuel plus Carbon costs |  | 3875000 | 4195000 | 4547000 | 4934200 | 5360120 | 6773632 | 7288995.2 | 7855894.72 | 8479484.192 | 9165432.6112 | 9919975.8723 | 12369973.4596 | 13282970.8055 | 14287267.8861 | 15391994.6747 | 16607194.1421 | 17943913.5563 | 19414304.912 | 21031735.4032 | 22810908.9435 | 0 | 0 | 0 | 0 | 0
SENSITIVITIES
| Capital | 100% |  | 32.5165 |  | 20% | Load plus 20% | Load -20%
|  | minus 10% | 4860000
|  | plus 20% | 6480000 |  |  | -19835839.5879 | -124806120.3286 | -85134441.1527
[6 empty] | 645642.5714 | 3873855.4285 | 2582570.2857
[7 empty] | 32.2175 | 32.965
| Fuel | 100% |  | 32.5165
|  | minus 10% | 3487500
|  | plus 20% | 4650000
| O&M | 100% |  | 32.5165
|  | minus 10% | 63000
|  | plus 20% | 84000