## Introduction
BANZ Technical Guide 14
Lifecycle analysis of heat plants
Introduction to financial model
This financial model provides the methodology and tools for calculating the LCOE (levelised cost of energy) from a range of fuel and technology options
It is a companion to the BANZ Technical Guide 14: Best practice guideline for life cycle analysis of heat plant projects
A description of the model is in Section 6 of the Guide, and
Detailed instructions for use are in Section 7 of the Guide
The Guide and this model can be downloaded from: |  | https://www.bioenergy.org.nz/resource/tg14-Life-cycle-analysis-heat-plant
Note:
This financial model has some cells hidden and others, not required for data input, will be locked in the final version,
but are left open during the consultation stage.

## Capital
BANZ Technical Guide 14
Lifecycle analysis of heat plants
Sheet 1: Capital costs
|  | Wood chip | Wood pellets | Diesel, fuel oil | Natural gas or LPG | Electricity (direct use) | Electricity (heat pump) | Coal
Boiler including fuel handling, de-ashing,emission control equipment and ancillary systems, or alternative heat plant
Per quotation |  | 1250000 | 1000000 | 850000 | 750000 | 200000 | 450000 | 1250000
Required to cover exclusions
Installation and commissioning
Spares, tools and stores
Heat distribution system cost
Sub total |  | 1250000 | 1000000 | 850000 | 750000 | 200000 | 450000 | 1250000
Ancillary and site works
Siteworks, civil costs, piling and foundations,
Fuel storage and processing: storage bin, reclaim system, drying, loaders, conveyors
Buildings: boiler house, control room, maintenance workshop, ablutions, lunchroom
Roading, paving, stormwater & landscaping
Water supply and treatment, effluent/sanitory disposal
Ash disposal systems, bins, handling equipment
Electrical supply interconnection
Security fencing, fire protection and alarm systems
Lighting, including security lighting
Remote control and monitoring systems
Integration of controls with existing plant
Sub total |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Consultants and services
Engineering and design
Geotech investigations and civil design
Mechanical, process and electrical
Environmental
Project management
Legal and building consents and other fees
Staff recruitment and training
Standard procedures, manuals & documents
Sub total |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Total, ex-contingencies |  | 1250000 | 1000000 | 850000 | 750000 | 200000 | 450000 | 1250000
Contingencies @ | 20% | 250000 | 200000 | 170000 | 150000 | 40000 | 90000 | 250000
Total including contingencies |  | 1500000 | 1200000 | 1020000 | 900000 | 240000 | 540000 | 1500000

## O&M
BANZ Technical Guide 14
Lifecycle analysis of heat plants
Sheet 2: Operating and maintenance costs
|  | Wood chip | Wood pellets | Diesel, fuel oil | Natural gas or LPG | Electricity (direct use) | Electricity (heat pump) | Coal
| Operations and maintenance staff | 120000 | 90000 | 25000 | 25000 | 1000 | 5000 | 120000
Parasitic electricity consumption
Other consumables
Maintenance contract
Annual plant shut/overhall
Callouts and breakages
Insurance
Ash disposal:
Cost of disposal (i.e. to landfill)
Service contractor costs
| Total annual cost | 120000 | 90000 | 25000 | 25000 | 1000 | 5000 | 120000

## Fuel
BANZ Technical Guide 14
Lifecycle analysis of heat plants
Sheet 3: Fuel costs
|  |  |  | Wood chip | Wood pellets | Diesel, fuel oil | Natural gas or LPG | Electricity (direct use) | Electricity (heat pump) | Coal
| Heat required (GJ) | 5000 |  | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000
|  | Heat production efficiency (gross) | % | 73% | 80% | 75% | 90% | 98% | 4 | 75% | COP in case of heat pumps
|  | Fuel requirement (calculated) | GJ | 6849.3151 | 6250 | 6666.6667 | 5555.5556 | 5102.0408 | 1250 | 6666.6667
|  | Fuel cost per GJ | $ | 10 | 15 | 30 | 26 | 47 | 47 | 8
|  | Annual cost of fuel (ex carbon cost) | $ | 68493.1507 | 93750 | 200000 | 144444.4444 | 239795.9184 | 58750 | 53333.3333
| Carbon emission cost | Emission factor (KT CO2/PJ) |  | 0 | 0 | 80 | 55 | 0 | 0 | 140
|  | Annual tonnes of CO2 |  | 0 | 0 | 533.3333 | 305.5556 | 0 | 0 | 933.3333
|  | Cost per tonne of CO2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
|  | Annual emmission cost |  | 0 | 0 | 13333.3333 | 7638.8889 | 0 | 0 | 23333.3333
|  | Total annual fuel cost |  | 68493.1507 | 93750 | 213333.3333 | 152083.3333 | 239795.9184 | 58750 | 76666.6667
|  |  |  | Wood chip | Wood pellets | Diesel, fuel oil | Natural gas or LPG | Electricity (direct use) | Electricity (heat pump) | Coal
Notes: |  | Typical fuel conversion efficiency, by fuel (gross) |  | In range 62 to 73%, dep. on moisture | 73% | 80-85% | 85% | Nominally 100% | COP say 3.5, up to 5 for commercial scale facilities | Up to 80%, depending on moisture content
|  | Indicative wood fuel calorific value (gross) |  | Seasoned chip: 30% moisture content, 13.5GJ/tonne
|  | Pinus radiaita |  | Partially seasoned chip: 40% mosture content, 11.5 GJ/tonne
Green wood chip: circa 50% mositure content, 8GJ/tonne

## Inputs
BANZ Technical Guide 14
Lifecycle analysis of heat plants
Sheet 4: Modelling inputs
|  | Wood chip | Wood pellets | Diesel, fuel oil | Natural gas or LPG | Electricity (direct use) | Electricity (heat pump) | Coal
INPUT FOR EACH FUEL SCENARIO
Total capital including contingencies |  | 1500000 | 1200000 | 1020000 | 900000 | 240000 | 540000 | 1500000
Total annual cost (O&M) |  | 120000 | 90000 | 25000 | 25000 | 1000 | 5000 | 120000
Annual fuel cost |  | 68493.1507 | 93750 | 213333.3333 | 152083.3333 | 239795.9184 | 58750 | 76666.6667
Assumed fuel inflation rate |  | 2% | 2% | 4% | 5% | 2% | 2% | 6%
Residual value (% of original cost) |  | 25% | 25% | 25% | 25% | 25% | 60% | 25%
Additional benefits/costs (NEGATIVE IF A COST) |  | 1000 | 1100 | 1200 | 1300 | 1400 | 1500 | 1600
Financial information (common)
WACC (real) | 6.8%
Project life (years) for modelling | 20

## Outputs
BANZ Technical Guide 14
Lifecycle analysis of heat plants
Sheet 5: Modelling outputs
| Scenario | Annual heat cost Year 1 | NPV (pre-tax) | Levelised heat cost per GJ
| Wood chip | 189493.1507 | -3559552.2331 | 66.1583
| Wood pellets | 184850 | -2259204.8309 | 41.9899
| Diesel, fuel oil | 239533.3333 | -4373967.4238 | 81.2951
| Natural gas or LPG | 178383.3333 | -3557627.8977 | 66.1226
| Electricity (direct use) | 242195.9184 | -3253984.0259 | 60.479
| Electricity (heat pump) | 65250 | -1474046.039 | 27.3968
| Coal | 198266.6667 | -4045888.4436 | 75.1974
Excluding
capital
| Sensitivities | Levelised heat cost per GJ
|  | Capital cost |  | Fuel cost |  | O&M
|  | Plus 20% | Minus 10% | Plus 20% | Minus 10% | Plus 20% | Minus 10%
| Wood chip | 71.7342 | 63.3704 | 67.4342 | 64.5634 | 68.0783 | 63.7583
| Wood pellets | 50.3879 | 37.7909 | 43.8757 | 39.6326 | 45.9244 | 40.0226
| Diesel, fuel oil | 82.8118 | 79.3994 | 85.9646 | 75.4583 | 97.8951 | 65.6226
| Natural gas or LPG | 67.4608 | 64.4498 | 69.7431 | 61.5969 | 66.5226 | 65.6226
| Electricity (direct use) | 60.8358 | 60.0329 | 64.946 | 54.8952 | 60.495 | 60.459
| Electricity (Heat pump) | 28.1997 | 26.3932 | 26.0288 | 27.3968 | 27.2968 | 27.3968
| Coal | 77.2782 | 72.5965 | 77.1869 | 72.7106 | 77.1174 | 72.7974

## Wood chip
BANZ Technical Guide 14
Lifecycle analysis of heat plants
Sheet 6, DCF model: | Wood chip
|  |  | Costs NPV |  | -3559552.2331
|  |  | Energy NPV |  | 53803.5476
|  |  | Levelised cost per GJ |  | 66.1583
Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Trigger Cell |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
Costs
Capital Cost of Plant | 1500000
Residual value |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -375000 | 0 | 0 | 0 | 0 | 0
Fuel cost |  | 68493.1507 | 69863.0137 | 71260.274 | 72685.4795 | 74139.189 | 75621.9728 | 77134.4123 | 78677.1005 | 80250.6425 | 81855.6554 | 83492.7685 | 85162.6239 | 86865.8763 | 88603.1939 | 90375.2577 | 92182.7629 | 94026.4182 | 95906.9465 | 97825.0855 | 99781.5872 | 0 | 0 | 0 | 0 | 0
O&M |  | 120000 | 120000 | 120000 | 120000 | 120000 | 120000 | 120000 | 120000 | 120000 | 120000 | 120000 | 120000 | 120000 | 120000 | 120000 | 120000 | 120000 | 120000 | 120000 | 120000 | 0 | 0 | 0 | 0 | 0
Additional benefits/costs |  | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0
Total annual costs | 1500000 | 189493.1507 | 190863.0137 | 192260.274 | 193685.4795 | 195139.189 | 196621.9728 | 198134.4123 | 199677.1005 | 201250.6425 | 202855.6554 | 204492.7685 | 206162.6239 | 207865.8763 | 209603.1939 | 211375.2577 | 213182.7629 | 215026.4182 | 216906.9465 | 218825.0855 | -154218.4128 | 0 | 0 | 0 | 0 | 0
Energy output (GJ) |  | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 0 | 0 | 0 | 0 | 0
SENSITIVITIES
| Capital |  |  | 66.1583
|  | minus 10% | 1350000 | 63.3704
|  | plus 20% | 1800000 | 71.7342
| Fuel |  |  | 66.1583
|  | minus 10% | 61643.8356 | 64.5634
|  | plus 20% | 82191.7808 | 67.4342
| O&M |  |  | 66.1583
|  | minus 10% | 108000 | 63.7583
|  | plus 20% | 144000 | 68.0783

## Wood pellets
DCF (Discounted Cash Flow) Analysis
Lifecycle analysis of heat plants
Sheet 7, DCF model: | Wood pellets
|  |  | Costs NPV |  | -2259204.8309
|  |  | Energy NPV |  | 53803.5476
|  |  | Levelised cost per GJ |  | 41.9899
Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Trigger Cell |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
Costs
Capital Cost of Plant | 1200000
Residual value |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -300000 | 0 | 0 | 0 | 0 | 0
Fuel cost |  | 93750 | 95625 | 97537.5 | 99488.25 | 101478.015 | 103507.5753 | 105577.7268 | 107689.2813 | 109843.067 | 112039.9283 | 114280.7269 | 116566.3414 | 118897.6682 | 121275.6216 | 123701.134 | 126175.1567 | 128698.6599 | 131272.633 | 133898.0857 | 136576.0474 | 0 | 0 | 0 | 0 | 0
O&M |  | 90000 | 90000 | 90000 | 90000 | 90000 | 90000 | 90000 | 90000 | 90000 | 90000 | 90000 | 90000 | 90000 | 90000 | 90000 | 90000 | 90000 | 90000 | 90000 | 90000 | 0 | 0 | 0 | 0 | 0
Additional benefits/costs |  | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 1100 | 0 | 0 | 0 | 0 | 0
Total annual costs | 1200000 | 184850 | 186725 | 188637.5 | 190588.25 | 192578.015 | 194607.5753 | 196677.7268 | 198789.2813 | 200943.067 | 203139.9283 | 205380.7269 | 207666.3414 | 209997.6682 | 212375.6216 | 214801.134 | 217275.1567 | 219798.6599 | 222372.633 | 224998.0857 | -72323.9526 | 0 | 0 | 0 | 0 | 0
Energy output (GJ) |  | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 0 | 0 | 0 | 0 | 0
SENSITIVITIES
| Capital | 100% |  | 41.9899
|  | minus 10% | 1080000 | 37.7909
|  | plus 20% | 1440000 | 50.3879
| Fuel | 100% |  | 41.9899
|  | minus 10% | 84375 | 39.6326
|  | plus 20% | 112500 | 43.8757
| O&M | 100% |  | 41.9899
|  | minus 10% | 81000 | 40.0226
|  | plus 20% | 108000 | 45.9244

## Diesel, fuel oil
DCF (Discounted Cash Flow) Analysis
Lifecycle analysis of heat plants
Sheet 8, DCF model: | Diesel, fuel oil
|  |  | Costs NPV |  | -4373967.4238
|  |  | Energy NPV |  | 53803.5476
81.2951
Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Trigger Cell |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
Costs
Capital Cost of Plant | 1020000
Residual value |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -255000 | 0 | 0 | 0 | 0 | 0
Fuel cost |  | 213333.3333 | 221866.6667 | 230741.3333 | 239970.9867 | 249569.8261 | 259552.6192 | 269934.7239 | 280732.1129 | 291961.3974 | 303639.8533 | 315785.4474 | 328416.8653 | 341553.54 | 355215.6816 | 369424.3088 | 384201.2812 | 399569.3324 | 415552.1057 | 432174.1899 | 449461.1575 | 0 | 0 | 0 | 0 | 0
O&M |  | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 0 | 0 | 0 | 0 | 0
Additional benefits/costs |  | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 0 | 0 | 0 | 0 | 0
Total annual costs | 1020000 | 239533.3333 | 248066.6667 | 256941.3333 | 266170.9867 | 275769.8261 | 285752.6192 | 296134.7239 | 306932.1129 | 318161.3974 | 329839.8533 | 341985.4474 | 354616.8653 | 367753.54 | 381415.6816 | 395624.3088 | 410401.2812 | 425769.3324 | 441752.1057 | 458374.1899 | 220661.1575 | 0 | 0 | 0 | 0 | 0
Energy output (GJ) |  | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 0 | 0 | 0 | 0 | 0
SENSITIVITIES
| Capital | 100% |  | 81.2951
|  | minus 10% | 918000 | 79.3994
|  | plus 20% | 1224000 | 82.8118
| Fuel | 100% |  | 81.2951
|  | minus 10% | 192000 | 75.4583
|  | plus 20% | 256000 | 85.9646
| O&M | 100% |  | 81.2951
|  | minus 10% | 81000 | 92.4951
|  | plus 20% | 108000 | 97.8951

## Natural gas or LPG
DCF (Discounted Cash Flow) Analysis
Lifecycle analysis of heat plants
Sheet 9, DCF model: | Natural gas or LPG
|  |  | Costs NPV |  | -3557627.8977
|  |  | Energy NPV |  | 53803.5476
66.1226
Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Trigger Cell |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
Costs
Capital Cost of Plant | 900000
Residual value |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -225000 | 0 | 0 | 0 | 0 | 0
Fuel cost |  | 152083.3333 | 159687.5 | 167671.875 | 176055.4688 | 184858.2422 | 194101.1543 | 203806.212 | 213996.5226 | 224696.3487 | 235931.1662 | 247727.7245 | 260114.1107 | 273119.8162 | 286775.8071 | 301114.5974 | 316170.3273 | 331978.8436 | 348577.7858 | 366006.6751 | 384307.0089 | 0 | 0 | 0 | 0 | 0
O&M |  | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 0 | 0 | 0 | 0 | 0
Additional benefits/costs |  | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300 | 0 | 0 | 0 | 0 | 0
Total annual costs | 900000 | 178383.3333 | 185987.5 | 193971.875 | 202355.4688 | 211158.2422 | 220401.1543 | 230106.212 | 240296.5226 | 250996.3487 | 262231.1662 | 274027.7245 | 286414.1107 | 299419.8162 | 313075.8071 | 327414.5974 | 342470.3273 | 358278.8436 | 374877.7858 | 392306.6751 | 185607.0089 | 0 | 0 | 0 | 0 | 0
Energy output (GJ) |  | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 0 | 0 | 0 | 0 | 0
SENSITIVITIES
| Capital | 100% |  | 66.1226
|  | minus 10% | 810000 | 64.4498
|  | plus 20% | 1080000 | 67.4608
| Fuel | 100% |  | 66.1226
|  | minus 10% | 136875 | 61.5969
|  | plus 20% | 182500 | 69.7431
| O&M | 100% |  | 66.1226
|  | minus 10% | 22500 | 65.6226
|  | plus 20% | 30000 | 66.5226

## Electricity (direct use)
BANZ Technical Guide 14
Lifecycle analysis of heat plants
Sheet 10, DCF model: | Electricity (direct use)
|  |  | Costs NPV |  | -3253984.0259
|  |  | Energy NPV |  | 53803.5476
|  |  | Levelised cost per GJ |  | 60.479
Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Trigger Cell |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
Costs
Capital Cost of Plant | 240000
Residual value |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -60000 | 0 | 0 | 0 | 0 | 0
Fuel cost |  | 239795.9184 | 244591.8367 | 249483.6735 | 254473.3469 | 259562.8139 | 264754.0702 | 270049.1516 | 275450.1346 | 280959.1373 | 286578.32 | 292309.8864 | 298156.0842 | 304119.2058 | 310201.59 | 316405.6218 | 322733.7342 | 329188.4089 | 335772.1771 | 342487.6206 | 349337.373 | 0 | 0 | 0 | 0 | 0
O&M |  | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0
Additional benefits/costs |  | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 1400 | 0 | 0 | 0 | 0 | 0
Total annual costs | 240000 | 242195.9184 | 246991.8367 | 251883.6735 | 256873.3469 | 261962.8139 | 267154.0702 | 272449.1516 | 277850.1346 | 283359.1373 | 288978.32 | 294709.8864 | 300556.0842 | 306519.2058 | 312601.59 | 318805.6218 | 325133.7342 | 331588.4089 | 338172.1771 | 344887.6206 | 291737.373 | 0 | 0 | 0 | 0 | 0
Energy output (GJ) |  | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 0 | 0 | 0 | 0 | 0
SENSITIVITIES
| Capital | 100% |  | 60.479
|  | minus 10% | 216000 | 60.0329
|  | plus 20% | 288000 | 60.8358
| Fuel | 100% |  | 60.479
|  | minus 10% | 215816.3265 | 54.8952
|  | plus 20% | 287755.102 | 64.946
| O&M | 100% |  | 60.479
|  | minus 10% | 900 | 60.459
|  | plus 20% | 1200 | 60.495

## Electricity (Heat pump)
BANZ Technical Guide 14
Lifecycle analysis of heat plants
Sheet 11, DCF model: | Electricity (heat pump)
|  |  | Costs NPV |  | -1474046.039
Plant replacement (years) | 15 |  | Energy NPV |  | 53803.5476
|  |  | Levelised cost per GJ |  | 27.3968
Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Trigger Cell |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
Costs
Capital Cost of Plant | 540000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 540000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Residual value |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -324000 | 0 | 0 | 0 | 0 | 0
Fuel cost |  | 58750 | 59925 | 61123.5 | 62345.97 | 63592.8894 | 64864.7472 | 66162.0421 | 67485.283 | 68834.9886 | 70211.6884 | 71615.9222 | 73048.2406 | 74509.2054 | 75999.3895 | 77519.3773 | 79069.7649 | 80651.1602 | 82264.1834 | 83909.467 | 85587.6564 | 0 | 0 | 0 | 0 | 0
O&M |  | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 0 | 0 | 0 | 0 | 0
Additional benefits/costs |  | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500 | 0 | 0 | 0 | 0 | 0
Total annual costs | 540000 | 65250 | 66425 | 67623.5 | 68845.97 | 70092.8894 | 71364.7472 | 72662.0421 | 73985.283 | 75334.9886 | 76711.6884 | 78115.9222 | 79548.2406 | 81009.2054 | 622499.3895 | 84019.3773 | 85569.7649 | 87151.1602 | 88764.1834 | 90409.467 | -231912.3436 | 0 | 0 | 0 | 0 | 0
Energy output (GJ) |  | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 0 | 0 | 0 | 0 | 0
SENSITIVITIES
Levelised cost per GJ
| Capital | 100% |  | 27.3968
|  | minus 10% | 486000 | 26.3932
|  | plus 20% | 648000 | 28.1997
| Fuel |  |  | Levelised cost per GJ
|  | 100% |  | 27.3968
|  | minus 10% | 52875 | 26.0288
|  | plus 20% | 70500 | 28.4912
O&M
|  | 100% |  | 27.3968
|  | minus 10% | 4500 | 27.2968
|  | plus 20% | 6000 | 27.4768

## Coal
BANZ Technical Guide 14
Lifecycle analysis of heat plants
Sheet 12, DCF model: | Coal
O&M | 120000
|  |  | Costs NPV |  | -4045888.4436
Capital cost | 1500000 |  | Energy NPV |  | 53803.5476
|  |  | Levelised cost per GJ |  | 75.1974
Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Trigger Cell |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
Costs
Capital Cost of Plant | 1500000
Residual value |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -375000 | 0 | 0 | 0 | 0 | 0
Fuel cost |  | 76666.6667 | 81266.6667 | 86142.6667 | 91311.2267 | 96789.9003 | 102597.2943 | 108753.1319 | 115278.3199 | 122195.019 | 129526.7202 | 137298.3234 | 145536.2228 | 154268.3962 | 163524.4999 | 173335.9699 | 183736.1281 | 194760.2958 | 206445.9136 | 218832.6684 | 231962.6285 | 0 | 0 | 0 | 0 | 0
O&M |  | 120000 | 120000 | 120000 | 120000 | 120000 | 120000 | 120000 | 120000 | 120000 | 120000 | 120000 | 120000 | 120000 | 120000 | 120000 | 120000 | 120000 | 120000 | 120000 | 120000 | 0 | 0 | 0 | 0 | 0
Additional benefits/costs |  | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 0 | 0 | 0 | 0 | 0
Total annual costs | 1500000 | 198266.6667 | 202866.6667 | 207742.6667 | 212911.2267 | 218389.9003 | 224197.2943 | 230353.1319 | 236878.3199 | 243795.019 | 251126.7202 | 258898.3234 | 267136.2228 | 275868.3962 | 285124.4999 | 294935.9699 | 305336.1281 | 316360.2958 | 328045.9136 | 340432.6684 | -21437.3715 | 0 | 0 | 0 | 0 | 0
Energy output (GJ) |  | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 0 | 0 | 0 | 0 | 0
SENSITIVITIES
| Capital | 100% |  | 75.1974
|  | minus 10% | 1350000 | 72.5965
|  | plus 20% | 1800000 | 77.2782
| Fuel | 100% |  | 75.1974
|  | minus 10% | 69000 | 72.7106
|  | plus 20% | 92000 | 77.1869
| O&M | 100% |  | 75.1974
|  | minus 10% | 108000 | 72.7974
|  | plus 20% | 144000 | 77.1174